附件：

广东省人民医院程控交换机及通信设备保养维护

项目院内比选要求

一、供应商相关资质要求：

1、供应商必须是具有独立承担民事责任能力的在中华人民共和国境内注册的法人。

2、单位负责人为同一人或者存在控股、管理关系的不同单位，不得参加同一采购项目报价。(供应商出具声明函)。

3、供应商需提供参加本次采购活动前3年内在经营活动中没有重大违法记录的书面声明。

4、本项目不接受联合供应商投标；不接受供应商项目分包、转包、挂靠。

5、供应商必须为NEC通信设备产品的正规代理商，且必须提供针对本项目的厂家授权以及技术服务授权，提供原厂供货证明及原厂质保承诺函。

6、供应商具备本项目相关的企业资质及技术服务能力。

二、全院通信设备系统维护配置清单：

以下为我院目前使用设备、线路类型以及使用情况，为便于保养维护，要求按照以下配置清单及厂家技术参数内容进行报价。
1.配置清单：

	序号
	项目名称
	数量
	单位
	备注

	1
	全院电话通讯主干线路保养维护
	9000
	线对/条
	含故障维修但不含重新敷设

	2
	全院线路、分线设备等保养维护（含分线箱、分线盒、配线间设备）
	72
	套
	

	3
	全院主配线架设备维护保养
	16000
	线对
	

	4
	全院电话机维护保养
	2400
	台
	不含新装电话

	5
	NEAX2400-IMX程控交换机维修保养(东川路)
	1800
	端口
	不含配件

	6
	NEAX8300程控交换机维修保养

(惠福分院)
	400
	端口
	不含配件

	7
	分机呼叫转移系统（东川路）
	32
	路
	不含配件

	8
	中继来显系统（东川路）
	50
	路
	不含配件

	9
	东病区光信号综合复用设备系统（东川路）
	4
	套
	不含配件

	10
	机房远程告警检测终端（东川路）
	1
	套
	不含配件

	11
	机房整流电源柜（东川路）
	1
	套
	不含配件


2.程控交换机技术参数及接口：

NEAX2400-IPX 电话接口以及数字接口传输接口参数

2.1 系统组织网络结构
PTT Network Configuration and PBX

[image: image1.png]PBX

LS: Local Switch

TS: Toll Switch
INTS: International
Switch

(M)

PTT Local Network PTT Toll Network PTT

International
Network

SPC:  Stored Program Control Exchange
XB: Cross-Bar Exchange

SXS:  Step-By-Step

Exchange M: Manual

Exchange





Type of Calls in the PTT Network

[image: image2.png]station

ordinary

Subscriber
A oTs: Outgoing TS
ITS: Incoming TS

+ Local Call —— Direct Dialing —E Ordinary Subscriber
Special Call —I: 119/110
1XX except above

Semi-Automatic (17X): (1) Station in PBX calls operator in OTS.
(2) The operator calls called party directly.

* Toll Call Automatic (Direct Dialing)

Manual (17X): (1) Station in PBX calls operator in OTS.
(2) The operator in ITS calls called party directly.

* International Automatic (International Subscriber
(Int’l) Call |
Dialing)Semi-Automatic (103)





2.2程控交换机数据传送握手信号
Transmit Sequence

[image: image3.png]ORIGINATING OFFICE TERMINATING OFFICE
(PBX) (LS)

Seizure

Seizure confirmation

Forward Signal (Sele, ting Signal)
1st Digit
Example of Register Signal
Transmit Sequence is
described in paragraph
2.2.4.
nth Digit
(n+1) th
Digit
—_—
or : Line Signal
Conversation ——
or : Register
______ Signal
Release *

Note : Outgoing/incoming signal interface for the Chinese No.1 line is Second Dial Tone only. Accordingly,
Forward Signal is sent regardless of Acknowledge signal.






Digital Interface Frame Configuration
[image: image4.png]1 Frame (8x32=256 —|
bits)

Time
slot 14 17 26 |27 | 28|29 3031
No.

Speech Channel 4| I— Speech Channel

Time Slot 0 is used for frame Time Slot 16 is used for Individual
synchronization. Line Signal (See below)

¢ Time Slot 16 Assignment for Frame 0

Remote Alarm Information Transfer (Multi-Frame
Synchronous Signal Alignment Loss).
Normal: 0 Alarm: 1

Bit No.

* Time Slot 16 Assignment for Frame 1-15

Bit No.

e HIHI

Bits No.1,2 and 3 are used for signal
Information Bit
(Refer to Table 2-4 through 2-7)





2.3远端模块接入系统信号参数

Digital Signal Coding of Line Signal (Local Call)
[image: image5.png]CODING

CONNECTION STATUS FORWARD BACKWARD | REMARKS
ar by a by,
Idle 1 0 1 0
Seizure 0 0 1 0
Seizure confirmation 0 0 1 1
Register signaling status 0 0 1 1
Answer 0 0 0 1
Called party replaces the handset first. 0 0 1 1
1 0 1 1
- Calling party replaces the handset last.
Calling 1 0 1 0
party
release 1 0 0 1
Calling party replaces the handset first. 1 0 1 1
1 0 1 0
0 0 1 1
Called party replaces the handset first. 1 0 1 1
Release }1::;; 1 0 1 0
method release 1 0 0 1
Calling party replaces the handset first. 1 0 1 1
1 0 1 0
0 0 1 1
Called party replaces the handset first. 1 0 1 1
Called 1 0 1 0
party
release | Calling party replaces the handset first. 1 0 0 1
1 0 1 1
Called party replaces the handset last.
1 0 1 0
Block 1 0 1 1






Digital Signal Coding of Line Signal(Toll/International Call-Automatic Outgoing)

[image: image6.png]CODING
CONNECTION STATUS FORWARD BACKWARD REMARKS
a by ay, by, Cp

Idle 1 0 1 0 1
Seizure 0 0 1 0 1
Seizure confirmation 0 0 1 1 1
Answer 0 0 0 1 1
Metering pulse 0 0 0 1 0

(150+30)

ms Pulse
Called party hangs up 0 0 1 1 1
Calling party hangs up 1 0 0 1 1
1 1 1
1 0 1
Block 1 0 1 1 1





	Digital   Signal   Coding   of   Line   Signal(Toll/international Call-Semi

	Automatic/Manual Outgoing)
	
	
	
	
	
	
	
	
	
	
	
	


[image: image7.png]CODING
CONNECTION STATUS FORWARD BACKWARD REMARKS
ar by ap by, Cp

Idle 1 0 1 0 1

Seizure 0 0 1 0 1

Seizure confirmation 0 0 1 1 1

. 1 0 1 1 1
Calling party hangs up before operator’s answer

1 0 1 0 1

Operator answer 0 0 0 1 1

Calling party hangs up 1 0 0 1 1

Before Operator ringing back 1 0 0 1 0

operator 0 0 1 1 1

drawing o

away Operator clears the circuit 1 0 1 1 1

1 0 1 0 1

After Conversation 0 0 0 1 1

operator 1 0 0 1 1

drawing Calling party hangs up 1 0 1 1 1

away 1 0 1 0 1

Block 1 0 1 1 1





Digital Signal Coding of Line Signal (Toll/International Call-Incoming

[image: image8.png]CONNECTION STATUS

Idle

CODING

FORWARD

BACKWARD

by

REMARKS

Seizure

Seizure confirmation

Register signaling

Answer

Called on hook

Re-ring

Forced release

Toll disconnection

| o ||l |o|o|loc|lo|oc|oc|o| O






2.4模块分机线路接入交换机需要满足的指标参数
[image: image9.png]Line conditions

ITEM SPECIFICATION
Station Loop Resistance 800 ohms max. (including telephone)
Line Impedance (Station/Trunk) 600 ohms

Leakage Resistance

More than 20000 ohms

C.0. Loop Resistance Less than 1700 ohms

Rotary Dial Pulse

ITEM RECEIVING SENDING
Dial Speed 9-22 pps 10 pps+0.8 pps
Break Ratio 55-77% (at 10 pps) 67+3% or 61+3%
Inter Digit Pause | 192 ms 200-1000 ms
DTMF signal
ITEM RECEIVING SENDING
Singal Duration More than 40 ms 64 ms or 128 ms
Inter Digit Pause More than 40 ms 62-240 ms
Signal Level -25 - 0 dbm -10dbm(low) — 9 dbm (high)
MFC-R2 signal
FORWAD DIRECTION BACKWARD DIRECTION
Fo 1380Hz 1140Hz
F1 1500Hz 1020Hz
F2 1620Hz 900Hz
F3 1740Hz 780Hz
F4 1860Hz 660Hz
F5 1980Hz 540Hz

Sensitive Range -35-0dbm

Ringing Signal
Voltage:90Vrms/75Vrms
Frequency:20Hz/25Hz

Transmission Loss
Station to Station: 0-1db
Station to COT:0 db
Station to DIT:0 db
Station to ODT:-4.5 db
Station to LDT:0 db
Trunk to Trunk:0 db





三、维护保养服务条款：

1、在日常维护中对医院整个电话线路系统进行分批、分期例行巡查，包括电话线路巡查、接线装置保养、线路系统抽测、总配线架保养，分线箱检查、配线间检查、电话接线、电话跳线。线路故障检修，话机故障检修。
2、设备维护保养单位对故障现场响应时间、故障修复时间作出以下承诺：对设备提供365天、24小时全天候应急处理服务，医院内有驻场人员驻守。接到报修通知后，设备维护保养单位技术人员必须在3小时内赶到现场，排除故障。对于一般的设备故障，保证不超过12小时排除。如确属系统严重故障，设备维护保养单位保证72小时内排除故障。如系统遇到不可抗拒因素造成全面停机，则由设备维护保养单位负责联系相关NEC厂家对设备进行全面检修。

3、设备维护保养单位保证控交换机零配件存货充足，与相关生产厂家合作良好，更换零配件货期尽可能当天到位，最迟不超过3天到位，否则免费为使用方提供代用零件并确保该系统的正常运行。

4、当系统发生现场技术人员无法排除的故障时，设备维护保养单位在1小时内派出具备排障技能的工程师赶赴现场处理。若设备在现场不能修复，可以免费提供代用设备。

5、按故障的发生频率，预先采购故障率较高、货期较长的设备，使需更换设备时能得以尽快更换，以确保系统设备的正常动作。

6、设备维护保养单位需配备高水平维修人员与充足配件，维保人员需具有NEC大型程控电话交换机的维保项目的经验。

7、设备维护保养单位每月至少1次派出保养人员对程控交换机系统进行例行保养、检查、测试、维修、排除故障隐患，确保设备保持安全、正常运行状态。

8、维护人员必须具备对程控电话交换机配套软件系统（计费系统、来电显示系统、呼叫转移系统等）熟练使用，需要时可以随时修改参数以达到使用要求。

9、根据程控电话交换机系统的实际运行情况，制定《程控电话交换机系统月度保养表》，对检查测试情况、对故障作出的维修及建议、保养维修后设备的动作状况、维保小结等工作细则认真作好记录，并经设备维护保养单位有关负责人签署后双方各留存一份。

10、设备维护保养单位应专门建立“用户维护档案”，并设立“用户维修卡”。每年会提交年度保养报告。
